YJV,YJLV  Cable amperemeter

| Serial number | Copper Wire Model | Single core current carrying capacity (25。C)(A) |  | voltage dropmv/M | Two-core ampacity (25。C)(A) |  | voltage dropmmv/M | Three-core current carrying capacity (25。C)(A) |  | voltage dropmmv/M | Four-core current carrying capacity (25。C(A) |  | voltage dropmmv/M |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | VV | YJV |  | VV | YJV |  | VV | YJV |  | VV | YJV |  |
| 1 | 1.5mm 2 /c | 20 | 25 | 30.86 | 16 | 16 |  | 13 | 18 | 30.86 | 13 | 13 | 30.86 |
| 2 | 2.5mm 2 /c | 28 | 35 | 18.9 | 23 | 35 | 18.9 | 18 | 22 | 18.9 | 18 | 30 | 18.9 |
| 3 | 4mm 2 /c | 38 | 50 | 11.76 | 34 | 38 | 11.76 | 23 | 34 | 11.76 | 28 | 40 | 11.76 |
| 4 | 6mm 2 /c | 48 | 60 | 7.86 | 40 | 55 | 7.86 | 32 | 40 | 7.86 | 35 | 55 | 7.86 |
| 5 | 10mm 2 /c | 65 | 85 | 4.67 | 55 | 75 | 4.67 | 45 | 55 | 4.67 | 48 | 80 | 4.67 |
| 6 | 16mm 2 /c | 90 | 110 | 2.95 | 70 | 108 | 2.9 | 60 | 75 | 2.6 | 65 | 65 | 2.6 |
| 7 | 25mm 2 /c | 115 | 150 | 1.87 | 100 | 140 | 1.9 | 80 | 100 | 1.6 | 86 | 105 | 1.6 |
| 8 | 35mm 2 /c | 145 | 180 | 1.35 | 125 | 175 | 1.3 | 105 | 130 | 1.2 | 108 | 130 | 1.2 |
| 9 | 50mm 2 /c | 170 | 230 | 1.01 | 145 | 210 | 1 | 130 | 160 | 0.87 | 138 | 165 | 0.87 |
| 10 | 70mm 2 /c | 220 | 285 | 0.71 | 190 | 265 | 0.7 | 165 | 210 | 0.61 | 175 | 210 | 0.61 |
| 11 | 95mm 2 /c | 260 | 350 | 0.52 | 230 | 330 | 0.52 | 200 | 260 | 0.45 | 220 | 260 | 0.45 |
| 12 | 120mm 2 /c | 300 | 410 | 0.43 | 270 | 410 | 0.42 | 235 | 300 | 0.36 | 255 | 300 | 0.36 |
| 13 | 150mm 2 /c | 350 | 480 | 0.36 | 310 | 470 | 0.35 | 275 | 350 | 0.3 | 340 | 360 | 0.3 |
| 14 | 185mm 2 /c | 410 | 540 | 0.3 | 360 | 570 | 0.29 | 320 | 410 | 0.25 | 400 | 415 | 0.25 |
| 15 | 240mm 2 /c | 480 | 640 | 0.25 | 430 | 650 | 0.24 | 390 | 485 | 0.21 | 470 | 495 | 0.21 |
| 16 | 300mm 2 /c | 560 | 740 | 0.22 | 500 | 700 | 0.21 | 450 | 560 | 0.19 | 500 | 580 | 0.19 |
| 17 | 400mm 2 /c | 650 | 880 | 0.2 | 600 | 820 | 0.19 |  |  |  |  |  |  |

Permissible continuous current carrying capacity of 8.7/10 (8.7/15) KV XLPE insulated power cable

| Rated voltageU。/U |  | 8.7/10(8.7/15)KV |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Model |  | YJV、YJLV、YJY、YJLY、YJV22、YJLV22、YJV23、YJLV23、JYV32,YJLV32、YJV33、YJLV33 |  |  |  | YJV、YJLV、YJY、YJLY |  |  |  |
| Number of cores |  | Three Cores |  |  |  | Single core |  |  |  |
| Laying |  | In the air |  | In soil |  | In the air |  | In soil |  |
| Conductor Material |  | copper | aluminum | copper | aluminum | copper | aluminum | copper | aluminum |
| Nominal cross section (mm2) | 25 | 120 | 90 | 125 | 100 | 140 | 110 | 150 | 115 |
|  | 35 | 140 | 110 | 155 | 120 | 170 | 135 | 180 | 135 |
|  | 50 | 165 | 130 | 180 | 140 | 205 | 160 | 215 | 160 |
|  | 70 | 210 | 165 | 220 | 170 | 260 | 200 | 265 | 200 |
|  | 95 | 255 | 200 | 265 | 210 | 315 | 240 | 315 | 240 |
|  | 120 | 290 | 225 | 300 | 235 | 360 | 280 | 360 | 270 |
|  | 150 | 330 | 225 | 340 | 260 | 410 | 320 | 405 | 305 |
|  | 185 | 375 | 295 | 380 | 300 | 470 | 365 | 455 | 345 |
|  | 240 | 435 | 345 | 445 | 350 | 555 | 435 | 530 | 400 |
|  | 300 | 495 | 390 | 500 | 395 | 640 | 500 | 595 | 455 |
|  | 400 | 565 | 450 | 520 | 450 | 745 | 585 | 680 | 520 |
|  | 500 | ... | ... | ... | ... | 855 | 680 | 765 | 595 |
| ambient temperature (℃) |  | 40 |  | 25 |  | 40 |  | 25 |  |

Steel-cored aluminium strandtechnical parameter

| Standard Section Aluminum/Steel （mm2） | Structure (Root/Diameter) （mm） |  | external diameter （mm2） | DC resistance is not greater than or equal to 20 degrees centigrade （Ω/km） | Calculating weight （kg/km） | Continuous Carrier Flow （A） |
| --- | --- | --- | --- | --- | --- | --- |
|  | aluminum | steel |  |  |  |  |
| 10/2 | 6/1.50 | 1/1.50 | 4.50 | 2.706 | 42.9 | 87 |
| 16/3 | 6/1.85 | 1/1.85 | 5.55 | 1.799 | 65.2 | 110 |
| 25/4 | 6/2.32 | 1/2.32 | 6.96 | 1.131 | 102.6 | 125 |
| 35/6 | 6/2.72 | 1/2.72 | 8.16 | 0.8230 | 141.0 | 145 |
| 50/8 | 6/3.20 | 1/3.20 | 9.60 | 0.5946 | 195.1 | 212 |
| 50/30 | 12/2.32 | 7/2.30 | 11.60 | 0.5692 | 372.0 | 250 |
| 70/10 | 6/3.80 | 1/3.80 | 11.40 | 0.4217 | 275.2 | 255 |
| 70/40 | 12/2.72 | 7/2.72 | 13.60 | 0.4141 | 511.3 | 340 |
| 95/15 | 26/2.15 | 7/1.67 | 13.61 | 0.3058 | 380.8 | 350 |
| 95/20 | 7/4.16 | 7/1.85 | 13.87 | 0.3019 | 408.9 | 360 |
| 95/55 | 12/3.20 | 7/3.20 | 16.00 | 0.2992 | 707.7 | 420 |
| 120/7 | 18/2.90 | 1/2.90 | 14.50 | 0.2422 | 379.0 | 380 |
| 120/20 | 26/2.32 | 7/1.85 | 15.07 | 0.2496 | 466.8 | 390 |
| 120/25 | 7/4.72 | 7/2.10 | 15.74 | 0.2345 | 526.6 | 400 |
| 120/70 | 12/3.60 | 7/3.60 | 18.00 | 0.2364 | 895.6 | 505 |
| 150/8 | 18/3.20 | 1/3.20 | 16.00 | 0.1989 | 461.4 | 442 |
| 150/20 | 24/2.78 | 7/1.85 | 16.67 | 0.1980 | 549.4 | 450 |
| 150/25 | 26/2.70 | 7/2.10 | 17.10 | 0.1939 | 601.0 | 470 |
| 150/35 | 30/2.5 | 7/2.50 | 17.50 | 0.1962 | 676.2 | 500 |
| 185/10 | 18/3.60 | 1/3.60 | 18.00 | 0.1572 | 584.0 | 497 |
| 185/25 | 24/3.15 | 7/2.10 | 18.90 | 0.1542 | 706.1 | 525 |
| 185/35 | 26/2.98 | 7/2.32 | 18.88 | 0.1592 | 732.6 | 525 |
| 185/45 | 30/2.80 | 7/2.80 | 19.6 | 0.1264 | 848.2 | 522 |
| 210/10 | 18/3.80 | 1/3.80 | 19.00 | 0.1411 | 650.7 | 523 |
| 210/25 | 34/3.33 | 7/2.22 | 19.98 | 0.1380 | 789.1 | 560 |
| 210/35 | 26/3.22 | 7/2.50 | 20.38 | 0.1363 | 853.9 | 590 |
| 210/50 | 30/2.98 | 7/2.98 | 20.86 | 0.1381 | 906.8 | 600 |
| 240/30 | 24/3.60 | 7/2.40 | 21.60 | 0.1181 | 922.2 | 610 |
| 240/40 | 26/3.42 | 7/2.66 | 21.66 | 0.1209 | 964.3 | 610 |
| 240/50 | 30/3.20 | 7/3.20 | 22.40 | 0.1189 | 1108 | 640 |
| 300/15 | 40/3.00 | 7/1.67 | 23.01 | 0.09724 | 939.8 | 650 |
| 300/20 | 45/2.93 | 7/1.95 | 23.43 | 0.09520 | 1002 | 655 |
| 300/25 | 48/2.85 | 7/7.22 | 27.76 | 0.09433 | 1058 | 690 |
| 300/40 | 24/3.99 | 7/2.66 | 23.94 | 0.09614 | 1133 | 705 |
| 300/50 | 26/3.83 | 7/2.98 | 24.26 | 0.09636 | 1210 | 725 |
| 300/70 | 30/3.60 | 7/3.60 | 25.20 | 0.09463 | 1402 | 740 |
| 400/20 | 42/3.51 | 7/1.95 | 26.91 | 0.07104 | 1286 | 800 |
| 400/25 | 45/3.33 | 7/2.22 | 26.64 | 0.07370 | 1295 | 800 |
| 400/35 | 48/3.22 | 7/2.50 | 26.82 | 0.07389 | 1349 | 810 |
| 400/50 | 54/3.07 | 7/3.07 | 27.63 | 0.07232 | 1511 | 815 |
| 400/65 | 26/4.22 | 7/3.44 | 28.00 | 0.07326 | 1611 | 850 |
| 400/95 | 30/4.16 | 19/2.32 | 29.14 | 0.07087 | 1860 | 873 |